## Sheet1
Energy Consumption basis pipe size: energy calculator program (clean water in new versus old pipe), Rev.5
Program: "PipeLoss"
by: Dr. Lev Nelik, P.E., Pumping Machinery, LLC, www.pumpingmachinery.com/pump_school/pump_school.htm - ref: Pump School theory and hands-on training sessions
Procedure (iterative):
1. Make a rough first guess assumption of the pump efficiency (80% is a good starting point)
2. Run "PipeLoss" program (enter flow, pipe length, pipe diameter, guessed efficiency) - obtain pipe friction loss, power, and energy consumption cost per year (non stop operation)
3. Run "PumpEff" program www.mj-scope.com/pump_tools/pump_efficiency.htm to adjust pump efficiency from flow and head (as calculated from "PipeLoss" program)
4. Re-Run "PipeLoss" program (using adjusted efficiency from "PumpEff" - obtain corrected pipe friction loss, power, and energy consumption cost per year (non stop operation)
5. Go back to Step 2 (usually one step is suffiently accurate)
| Flow, gpm | Pipe Length, ft | Pipe Dia, in | Pump Efficiency, % | % time operation per year | A, in2 | Velocity, ft/sec | Friction Losses, ft | Pump Head, ft | Power, BHP | Yearly Energy Cost, $
| a. Friction based system - typical new pipe (enter five values into a table on the left) | [5 empty] | Table on right (answers)
basis: | 8000 | 26250 | 18 | 80% | 100% | 254.34 | 10.0967 | 418.1288 | 418.1288 | 1055.8807 | 690013.8156
trials: | 8000 | 26250 | 18 | 80% | 100% | 254.34 | 10.0967 | 418.1288 | 418.1288 | 1055.8807 | 690013.8156
| b. Friction based system - typical old pipe (enter five values into a table on the left) | [5 empty] | Table on right (answers)
basis: | 8000 | 26250 | 18 | 80% | 100% | 254.34 | 10.0967 | 836.2575 | 836.2575 | 2111.7614 | 1380027.6312
trials: | 8000 | 26250 | 18 | 80% | 100% | 254.34 | 10.0967 | 836.2575 | 836.2575 | 2111.7614 | 1380027.6312
Note: systems can also be:
a. Friction only (additional turns, elbows, bends, restrictions can be estimated via equivalent pipe lengths)
b. Static Head only
c. Combination of both