## Sheet1
Centrifugal Pump: Typical Expected Efficiency Estimator (Courtesy and Copyright of www.PumpingMachinery.com) |  |  |  |  | Hydraulic Institute (Typically Expected) Efficiency Chart:
(You can change only entries in shaded blue areas - the results recalculate automatically)
US Units |  |  | Metric Units
Pump Flow, GPM | 1111 |  | Pump Flow, m3.hr | 454.2357
Total Pump Head, feet | 1234 |  | Total Pump Head, meters | 376.1278
Specific Gravity, SG | 1 |  | Specific Gravity, SG | 1
Number of Stages | 1 |  | Number of Stages | 6
Speed, RPM | 3600 |  | Speed, RPM | 3600
Head per stage, feet | 1234 |  | Head per stage, meters | 62.688
~ Impeller Diameter, inches | 16.4818 |  | ~ Impeller Diameter, mm | 209.7349
Specific Speed (US), Ns | 576.3326 |  | Specific Speed (US), Ns | 2964.453
Specific Speed (metric), ns | 11.1692 |  | Specific Speed (metric), ns | 57.4506
Specific Speed (universal), Ωs | 0.21088 |  | Specific Speed (universal), Ωs | 1.0847
Efficiency, % | 72.11% |  | Efficiency, % | 83.48%
Power, HP | 480.1224 |  | Power, KW | 556.9425
Useful Formulas:
Single-Stage Centrifugal Pump |  | Multi-Stage Centrifugal Pump
For more information on Pumps, visit Pump School section of www.PumpingMachinery.com
Concept of Pump Head Concept:
For more information on Pumps, visit Pump School section of www.PumpingMachinery.com
FLOW:
• GPM / 4.403 = M3/HR
• GPM / 15.9 = liters/sec
VELOCITY:
* FT/SEC = gpm x 0.321 / (π x in2 / 4)
* M/SEC = m3/hr x 277.8 / (π x mm2 / 4) = m3/hr x 0.43 / (π x in2 / 4)
PRESSURE:
* PSI / 14.7 = atm
• PSI / 14.2 = kg/cm2
• kg/cm2 = atm / 1.033
• PSI / 14.5 = Bars
• PSI / 145 = MPa
HEAD:
• FEET = psi x 2.31 / SG
• METERS = atm x 10.3 / SG = kg/cm2 x 10.0 /SG
POWER:
• BHP = gpm x ft x SG / 3960 / EFF
• KW = m3/hr x m x SG / (367.5 x EFF)
• HP x 0.746 = KW