## Centrifugal pump
Sample example of a 2-branch system with a single centrifugal pump |  |  |  | gravitational constant g = | 32.2
|  |  |  | sg = | 1
First pipe branch:
Equivallent pipe length L1, ft = | 200 |  |  | A1, in2 = | 7.065
Pipe Diamater D1, in = | 3 |  |  | f 1= | 0.03
|  |  |  | k1, friction in branch 1 | 0.00039841
Second pipe branch:
Equivallent pipe length L2, ft = | 200 |  |  | A2, in2 = | 7.065
Pipe diameter D2, in = | 3 |  |  | f 2= | 0.03
|  |  |  | k2, friction in branch 2 | 0.00039841
Pump Performance Curve:
Zero flow Q0, gpm = | 0 | Zero flow head H0, ft = | 42 | n= | 1.7565
50% flow Q50, gpm = | 200 | Head at 50% flow H50, ft = | 34 | a= | -0.00072677
BEP flow Q100, gpm = | 500 | BEP head H100, ft = | 2 | b= | 42
h1, feet - static head of water in tank 1 | 10
h2, feet - static head of water in tank 2 | 2
Q, gpm - guess until error_Q is small | 360
hpump, feet - calculated from H-Q curve | 19.537
Flow thru branch 1, Q1, gpm | 154.7185
Flow thry branch 1, Q2, gpm | 209.8044
Qresult, gpm (Q = Q1+Q2) | 364.5229
error_Q | 1.241%
Back to Article 39

## PD pump
Sample example of a 2-branch system with a single positive displacement pump
k1, friction in branch 1 | 0.002 | enter as desired
k2, friction in branch 2 | 0.003 | enter as desired
h1, feet - static head of water in tank 1 | 10 | enter as given
h1, feet - static head of water in tank 1 | 2 | enter as given
Q, gpm - given | 120 | enter as given
hguess, feet - keep changing until error_Q is small | 15.6 | guess
Q1, gpm | 52.915 | calculated
Q2, gpm | 67.33 | calculated
Qresult, gpm | 120.2451 | calculated
error_Q | 0.2038% | calculated
Back to Article 39