Elfer     Inc.   (

Maintenance Guidelines, Machinery Reliability Programs

# For a complete Book contact:

Luis F. Rizo, PE				Phone: 518-371-0683

4 Mates Way 				Fax: 518-371-0683

Waterford, New York 12188-1165		http://www.elfer.com

Article #62:  Recommended preventive maintenance checks for centrifugal pumps and drives

| Interval | Routines | Date/Initial |
| --- | --- | --- |
| Daily | Check pump for noisy bearings and cavitation. |  |
| Daily | Check bearing oil for water and discoloration. |  |
| Daily | Feel all bearings for temperature. |  |
| Daily | Inspect bearings and oil rings through filling ports. Wipe bearing covers clean. |  |
| Daily | Check oil leaks at the gaskets. |  |
| Daily | Self flush pumps - Hand check the flush line temperature to determine flow through the line. External flush pumps - Determine if flow indicator and needle valve adjustment are functioning properly. |  |
| Daily | Determine if the mechanical seal conditions are normal. |  |
| Daily | Check any water cooling for effective operation. Hand test differential across coolers, jackets and exchangers. Disassemble and clean as required. |  |
| Daily | Check the operability of the heat tracing. |  |
| Daily | Determine if steam leakage at packing and glands is normal. |  |
| Daily | Check for leaks at pressure casing and gaskets. Determine if steam traps are operating properly - no continuous blow & water in casing or drain. |  |
| Monthly | Add oil to the bearing reservoirs, if required. |  |
| Monthly | Clean oiler bulbs and level windows as required. |  |
| Monthly | Make sure that the oil level is the correct distance from the shaft centerline. Adjust if necessary. |  |
| Monthly | Clean out debris from bearing brackets. Drain hole must be open. |  |
| Monthly | Change oil in hydraulic governors. |  |
| Monthly | Determine if hydraulic governor heater is working. |  |
| Monthly | Check for proper oil level & leaks at hydraulic governor. Check for oil leaks at lines, fittings & power piston. |  |
| Monthly | Replace guards (repair if required). |  |
| Monthly | Determine if pump unit requires general cleaning by others. |  |
| 6 Months | Machines not running - Standby service: Overfill bearing housing to bottom of the shaft and rotate several turns by hand to coat the shaft and the bearing with oil. |  |
| 6 Months | Apply a light coat of rust preventive product to expose machined surfaces to prevent rust and corrosion. |  |
| 6 Months | Clean & oil governor linkage & valve stems. |  |
| 6 Months | Exercise overspeed trip & valve steam linkage on turbines not running. |  |
| Yearly | Thoroughly inspect disc coupling for signs of wear & cracks in laminations. Tighten bolts. |  |
| Yearly | Using a dial indicator, check the coupling alignment with the equipment coupled. Use special coupling indicator clamps where possible. Ensure that thermal growth allowance is correct. |  |
| Yearly | Using an indicator clamped on the coupling, depress and lift on each coupling and note the dial indicator change. Determine if the deflection is normal for this machine. Refer to OEM manual. |  |
| Yearly | Using an indicator, check axial float of the pump & the driver shaft in similar manner. |  |
| Yearly | Remove turbine sentinel valve. Shop test & adjust to proper setting. |  |
| Yearly | Inspect trip and throttle valve stems and their linkages for wear. Check over-speed mechanism for wear. (Turbine must be down). |  |
| Yearly | Remove mechanical the governor cover & inspect flyball seat, spring, bearing & plunger for wear. |  |

| Yearly | Uncouple from pump & overspeed turbine. Ensure that trip valve will stop turbine with steam supply valve (throttle valve) fully open. Compare tripping speed with previous records. Adjust trip mechanism & repeat procedure. Follow manufacturer’s instructions when making adjustments. |  |
| --- | --- | --- |
| Yearly | Where the process will allow it, test run the turbine coupled to the pump. When not possible, run the turbine uncoupled. With a tachometer ( verify proper governor operation & control. Determine if hand (booster) valves are completely closed when required to carry load. This influences steam economy. |  |
| Seasonal |  |  |
| Fall & Summer | Do a seasonal oil change out, if required by OEM lubrication guide. |  |
| Fall | Where cooling water is decommissioned, ensure that no water remains in the jackets, coolers and piping. |  |
| Fall | Inspect for damaged or missing insulation |  |
| Fall | Reestablish steam flow or electrical tracing continuity. |  |

| Illustrations of maintenance checks1 |  |
| --- | --- |
| 1. Oil level check | 2. Re-greasing of bearings |
| 3. Shaft to bearing housing face runout | 4. Shaft end play measurement |

1 Pictures courtesy of Goulds Pumps

Copyright ( Elfer, Inc. 1998, Waterford, New York

Centrifugal pumps fits and clearance checklist. Basic data

| No: | Measurement | Tolerance |
| --- | --- | --- |
|  | Ball bearing inside diameter (I. D.) to shaft. | 0.0001" to 0.0007" (0.003mm to 0.018mm) interference. |
|  | Ball bearing outside diameter (O. D.) to housing. | 0.0001" to 0.001" (0.003mm to 0.03mm) clearance. |
|  | Sleeve to shaft. | 0.001" to 0.0015" (0.03mm a 0.04mm) clearance. |
|  | Impeller to shaft. | Metal to metal fit to 0.0005" (0.13mm) clearance. |
|  | Note: there are pumps such as horizontal, axial split pumps interference fits. Consult your OEM manual | and multi-stage vertical pumps that have |
|  | Throat bushing |  |
|  | Throat bushing to case. | 0.002" to 0.003" (0.05mm a 0.08mm) interference. |
|  | Throat bushing to shaft. | 0.015" to 0.020" (0.40 a 0.51mm) clearance. |
|  | The throat bushings on some vertical in-line pumps act as clearances. | intermediate bearings and require closer. |
|  | Impeller |  |
|  | Impeller ring to hub. | 0.002" to 0.003" (0.05mm a 0.08mm interference. |
|  | The impeller ring is normally doweled or spot in at least two | places welded |
|  | Impeller ring to case ring clearance. | 0.010" to 0.012" (0.254mm a 0.3mm) plus 0.001" (0.03mm) per in. (25.4mm) of impeller ring diameter up to a 12" (3,658mm) ring. Add 0.0005 (0.013mm) per inch (25.4mm) of ring diameter over 12" (3,658mm). For temp. ( 500 ( (260(C) add 0.10" (2.54mm). Also add 0.005 (0.127mm) for galling materials (stainless steel). |
|  | Renew impeller rings when clearance reaches twice original clearance. |  |
|  | Case rings |  |
|  | Case rings are not to be bored out larger than 3% of original diameter. |  |
|  | Case ring to case. | 0.002" to 0.003" (0.05mm a 0.08mm) interference. |
|  | The case ring is normally doweled or spot welded in | at least two places. |
|  | Oil deflector to shaft. | 0.002" to 0.003" (0.05mm a 0.08mm) clearance. Install "O" ring in the ID if possible. |
|  | Packing gland |  |
|  | Packing gland to shaft. | 1/32" (0.8mm) clearance. |
|  | Packing gland to stuffing box bore. | 1/64" (0.016mm) clearance. |
|  | Lantern ring | . |
|  | Lantern ring to shaft. | 0.015" to 0.020" (0.40mm a 0.51mm) clearance. |
|  | Lantern ring to stuffing box. | 0.005" to 0.010" (0.13mm a 0.25mm) clearance. |
|  | Coupling to shaft. | Metal to metal to 0.0005 (0.013mm) clearance. |

| 12. | Seal gland |  |
| --- | --- | --- |
|  | Seal gland alignment boss to stuffing box. | 0.002" to 0.004" (0.05mm a 0.10mm) clearance. |
|  | Seal gland throttle bushing to shaft. | 0.018" to 0.020" (0.5mm to 0.51mm) clearance, unless otherwise specified for hot pumps. |
|  | Seal locking collar to shaft. | 0.002" to 0.004" (0.05mm a 0.10mm) clearance |
|  | Seal spring compression. | 7/8" (22.2mm) long springs - 3/16"(4.8mm). |
|  | ( | ¾" (12.5mm) long springs - 5/32"(4.0mm) |
|  | Seal spring compression. | 1/2"(12.7mm) short springs - 1/16" (1.6mm) unless otherwise specified by the manufacturer. |
|  | Rotating and stationary seal rings. | Sealing surfaces to be flat within 3 Helium light bands |
|  | Heads, case, suction cover, bearing housing to case alignments fits. | 0.004" (0.01mm) maximum clearance. Use dial indicator and feeler gauges to correct fit-up and alignment. |

Horizontal axial split case

1.	Stationary parts fit case metal to metal to 0.004" (0.01mm) clearance.

2.	Measure and inspect case fits for wear and corrosion.  Repair by building up and re-machining.

3.	All other repairs same as vertical radial split case pumps except: Case rings to be bored in a jig not chucked.

4.	Align element in case with feeler gauges and dial indicator.  Dowel bearing housing in place after alignment.

5.	When cutting gaskets for horizontal split pumps, cut bolt hole openings on head and split gasket lengthwise.  Cut the rest of the gasket on the case with all the slack in the boltholes pulled to the outside edges.  Leave stuffing box gasket length long and trim after head has been set in place and tightened.

OVERHUNG IMPELLER, SEPARATELY COUPLED, SINGLE STAGE, FRAME MOUNTED

| 1 Casing | 18 Bearing, outboard | 47 Seal, bearing cover, inboard |
| --- | --- | --- |
| 2 Impeller | 19 Frame | 49 Seal, bearing, cover, outboard |
| 6 Shaft, pump | 22 Locknut, bearing | 67 Shim, frame liner |
| 11 Cover, stuffing box | 29 Ring, lantern | 69 Lockwasher |
| 13 Packing | 37 Cover, bearing | 71 Adapter |
| 16 Bearing, inboard | 40 Deflector | 73 Gasket |
| 17 Gland | 46 Key, coupling |  |

# Endnotes

Courtesy of the Hydraulic Institute Standards.

Copyright ( Elfer, inc. 1998, Waterford, New York

Back to PUMP MAGAZINE Page